## RFI #001
Request for Information #001
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Electrical power plans not issued | Electrical |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
Please issue the electrical power plans (receptacles, switches, homeruns, equipment circuits for the 8 WSHP units, EF-2/EF-3, the dumbwaiter, hand dryers, the grease recovery device and the HWR pump): E-2.0 is an all-existing single line, E-2.1 holds panel schedules only and Addendum 3 gives panel locations only. Sheets / documents: E-2.0, E-2.1, E-2.2, Addendum 3. Bid impact: Bid-letter item Other required scope (electrical power): rewiring of 6 existing panels (116 circuits, E-001..E-006, E-013), equipment branch circuits (E-014..E-021, E-023, E-024) and electrical demolition (E-025) cannot be quantified; only devices and connections are priced.
Suggestion:
Issue E-3.x power plans with circuit numbers, or confirm that branch circuiting is design-build by the electrical contractor from the panel schedules.
Answer: |  |  |  | Date Answered:

## RFI #002
Request for Information #002
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Condenser-water loop for the WSHP units | Mechanical |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
M-1 schedules eight water-source heat pumps at 50 F EWT (16/24/30 GPM each) but no condenser-water loop piping, loop pump, heat-rejection equipment or water source is shown on any M- or P-sheet: please issue the loop design (source, routing, pipe sizes, pump, heat rejection, hose kits and valves). Sheets / documents: M-1, M-2, P-1..P-7. Bid impact: Bid-letter item Mechanical: line M-004 (condenser-water piping and loop equipment) is not quantifiable, and the plumbing and electrical connections for a loop pump / heat-rejection unit are not in any trade's bid.
Suggestion:
Issue M-3/M-5 with the loop schematic and equipment schedule, or confirm the units tie into an existing building condenser-water loop and where the points of connection are.
Answer: |  |  |  | Date Answered:

## RFI #003
Request for Information #003
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Mezzanine mechanical plan (M-3 / M-5) not in the set | Mechanical |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
No mezzanine mechanical plan (M-3) or M-5 is in the bid set: please issue the sheets that locate WSHP-1 through WSHP-7, EF-2 and EF-3, their supply/return/exhaust ductwork, the dishwasher exhaust duct route (A-2.20 KN11) with its floor opening (A-1.20 KN18, tag not found on the plan), the toilet exhaust duct, thermostat / CO2 sensor locations and damper counts. Sheets / documents: M-1, M-2, A-2.20 KN11, A-1.20 KN18. Bid impact: Bid-letter item Mechanical: lines M-031, M-032, M-033 (mezzanine ductwork, dishwasher exhaust duct, duct insulation), M-007 (thermostats), M-041..M-043 (dampers, flex) and Demolition line D-18 (floor opening for the dishwasher exhaust) are not quantifiable.
Suggestion:
Issue M-3 (mezzanine plan) and M-5 (attic / roof plan) at 3/16 in scale with duct sizes.
Answer: |  |  |  | Date Answered:

## RFI #004
Request for Information #004
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Furnished-by / installed-by split of the K2.0 equipment schedule | Foodservice |  |  | Scope
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
K2.0 has no furnished-by / installed-by columns and no K.E.C. / G.C. symbols although its legend and KN notes 12 and 23 refer to them: please issue the furnish / install split (KEC furnish and install, KEC furnish / GC install, owner, vendor) for all 95 scheduled items, including the mop sink (item 19) and hand sinks (items 31, 71, 93) that K0.0 notes J and L word as GC and KEC scope respectively. Sheets / documents: K2.0 (legend, KN notes 12 and 23), K0.0 notes J and L. Bid impact: Bid-letter items F&B equipment and Owner-provided equipment install: 82 equipment lines are at quote with no furnishing party, so the dealer package, the GC's setting labor and the plumbing / electrical final connections (P-064, P-066, E-014, E-015) cannot be assigned or priced.
Suggestion:
Add F/I columns to K2.0 or issue the symbol key the KN notes refer to.
Answer: |  |  |  | Date Answered:

## RFI #005
Request for Information #005
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Fire sprinklers: new NFPA-13 system vs modification of the existing system | Fire protection |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-0.00 states the sprinkler system as 'Yes - New NFPA-13' while A-0.21 states 'Yes existing, compliance with NFPA-13': please confirm whether a new NFPA-13 system or a modification of the existing system is required, and who prepares and permits the FLS / sprinkler plans. Sheets / documents: A-0.00, A-0.21, M-1 (plan-check note). Bid impact: Bid-letter item Other required scope: line G-04 (modified fire-sprinkler and FLS plan submittal) cannot be scoped and no sprinkler head, piping or design-build quantity exists; a new system is a major cost item for the fire-sprinkler subcontractor and affects ceiling and framing sequencing.
Suggestion:
State the sprinkler scope on A-0.00 and issue the FLS submittal requirements.
Answer: |  |  |  | Date Answered:

## RFI #006
Request for Information #006
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Contract duration, schedule and phasing constraints | General |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
No contract duration, milestone schedule or phasing requirement is in the bid documents, while the exit-stair work is inside the occupied 1704 N Vine restaurant (permit 09016-10000-04328, occupant load 90): please state the required duration, start date, working-hours limits and the phasing of work inside the occupied restaurant. Sheets / documents: A-0.00, A-0.20 (exit stair), bid instructions. Bid impact: Bid-letter item Other required scope: every duration-driven general-conditions line (G-21 phasing, G-22 temporary facilities, G-23 daily clean-up, G-24 supervision and project management) is not quantifiable without a duration.
Suggestion:
Issue a bid-form duration or allow bidders to state their own schedule.
Answer: |  |  |  | Date Answered:

## RFI #007
Request for Information #007
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
WSHP count, tonnage and schedule data | Mechanical |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
M-1 schedules 8 water-source heat pumps (5 x 50VQP072, 2 x 50VQP096, 1 x 50HQP120 = 56 tons nominal) while the M-1 Cal Green system description says '(2) water source heat pump units ... 12-tons' and A-2.20 KN14 tags 4 HVAC units, the WSHP-4/5 row repeats the 072 capacity / weight / MOCP data and the air balance lists WSHP-8 at 2400 CFM vs 4000 CFM in the schedule with totals that do not sum: please confirm the unit count, models and corrected schedule. Sheets / documents: M-1 (WSHP schedule, Cal Green note, air balance), A-2.20 KN14. Bid impact: Bid-letter items Mechanical and Other required scope (electrical power): lines M-001..M-003 (8 units), M-005 (condensate), E-017 (8 branch circuits, MCA 21.2 / 31.0 / 44.3 A) and the loop (M-004) all depend on the unit count and sizes.
Suggestion:
Re-issue the M-1 WSHP schedule and air-balance table.
Answer: |  |  |  | Date Answered:

## RFI #008
Request for Information #008
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Type-I exhaust fan EF-1 and K2.0 item 57 exhaust fan system | Mechanical / Foodservice |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
M-1 keeps the existing EF-1 (3000 CFM @ 2.75 in SP, static calc at 2975 CFM) and MUA-1 (3600 CFM) while the hoods on M-6 / K7.0 require 2773 + 1819 = 4592 CFM and the M-1 plan-check note cites 1900 CFM 'actual', and K2.0 item 57 schedules a new 'EXHAUST FAN SYSTEM 1 LOT, SEE HOOD DRAWINGS' (208 V 3 ph, amps '*') with no fan or MUA data on K7.0 / K7.1: please confirm whether EF-1 and MUA-1 are replaced, who furnishes any new fans, and the scope of the design-build survey / repair of the existing units. Sheets / documents: M-1 (EF-1, MUA-1 schedules, plan-check note), M-6, K2.0 item 57, K7.0/K7.1. Bid impact: Bid-letter items Mechanical and F&B equipment: lines M-008, M-009, M-047 (existing fans, survey and repairs), FE-57 (fan lot) and the hood vendor package cannot be priced; the electrical feed (E-016, 480 V vs 208 V) depends on the answer.
Suggestion:
Issue the CaptiveAire fan / MUA schedule or state that EF-1 and MUA-1 remain as scheduled on M-1 and item 57 is void.
Answer: |  |  |  | Date Answered:

## RFI #009
Request for Information #009
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Type-I hood length | Mechanical / Foodservice |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
M-6 and K7.0 give Hood 1 as 10'-1" + 8'-1" = 18'-2" (18'-3" overall with the 1 in end standoff) while the hood outlines on M-2 scale to 6'-8" + 7'-6" = 14'-2" and A-2.10 shows about 13 ft: please confirm the hood lengths and the cooking-line length they must cover. Sheets / documents: M-6, K7.0/K7.1, M-2, A-2.10. Bid impact: Bid-letter items F&B equipment, Mechanical and Interior walls: hood lines FE-56.1 / FE-56.2 / M-012 / M-013 / M-015, the fire-suppression nozzle count (FE-55 / M-016), the MUA / exhaust airflow, the grease-duct riser sizes (M-019) and the wall flashing (FE-58) and backing behind the cooking line all depend on the length.
Suggestion:
Confirm the K7.0 lengths (18'-3") govern and correct M-2 / A-2.10.
Answer: |  |  |  | Date Answered:

## RFI #010
Request for Information #010
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Sound / AV, TV, data and telecom scope | Low voltage |  |  | Scope
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
Addendum 3 notes three new panels 'to manage lighting and sound' and the Dillons panel to be removed carries 7 TV-outlet and 3 POS circuit lines, but no sound / AV system, TV / video distribution, data / telecom cabling, network rack or security device is drawn on any sheet: please state whether any low-voltage system other than the POS J-boxes (K2.0 item 68) is in the general contractor's bid and issue its drawings. Sheets / documents: Addendum 3 (new panels note), E-2.1 (Dillons, KC, EPB schedules), K2.0 item 68. Bid impact: Bid-letter item Low Voltage: lines LV-001 (sound / AV), LV-003 (TV outlets), LV-004 (data / telecom) and LV-006 (security) carry no quantity; a stage sound system is a major cost that cannot be priced or excluded with certainty.
Suggestion:
State 'AV, sound, TV and data by owner's vendor; GC provides conduit / backing only' or issue T-series drawings.
Answer: |  |  |  | Date Answered:

## RFI #011
Request for Information #011
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Grease duct in the existing rated shaft | Mechanical |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
M-4 section B shows a P.O.C. to '(E) grease duct @ top of shaft' inside an 'existing fire rated shaft' with the section broken between levels 05 and 13, while the M-1 static calculation assumes 125 ft of 16 in duct plus 350 ft of 48 x 18 duct: please confirm whether the shaft duct is new or existing, the shaft height from level 02 to the roof, the cleanout count and the extent of field-applied fire wrap. Sheets / documents: M-4 (section B), M-1 (static calc), M-2. Bid impact: Bid-letter item Mechanical: lines M-020 / M-021 (grease duct main and shaft riser, 62 LF drawn is not the shaft height), M-022 (fire wrap) and M-023 (cleanouts) cannot be quantified.
Suggestion:
Issue a full-height shaft section or state the duct sizes and lengths of the M-1 calculation as the design quantities.
Answer: |  |  |  | Date Answered:

## RFI #012
Request for Information #012
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Duct sizes and air-device tags on M-2 | Mechanical |  |  | Unreadable / incomplete
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
M-2 prints no duct sizes, gauges or air-device tags (widths were scaled from the drawing; depths are unknown) and the plan draws 23 untagged outlets plus 5 untagged symbols on the attic RCP A-3.22 against 16 devices scheduled on M-1 (A3, B4, C6, D1, E1, F1): please issue duct sizes and tag every air device. Sheets / documents: M-2, M-1 (air-distribution schedule), A-3.22. Bid impact: Bid-letter item Mechanical: ductwork lines M-024..M-030 (230 LF drawn) cannot be weighed for pricing, insulation M-033 has no SF, and air devices M-034..M-040 / M-050 cannot be reconciled (23 + 5 drawn vs 16 scheduled).
Suggestion:
Re-issue M-2 with duct sizes and device tags.
Answer: |  |  |  | Date Answered:

## RFI #013
Request for Information #013
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Mezzanine prep-bar equipment schedule | Foodservice / Plumbing |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The mezzanine prep-bar (room 24) shows units tagged Q-270, 18-53C, TBB-24GAL-72, 32-ST, a multi-compartment sink and a hand sink on A-5.20 and Addendum 1, P-4 tags BS-3 / BS-4 / BS-5 as items B1 / B3 / B5, and the P-6 water-heater calculation lists a bar triple sink, a glass washer and an 18 x 18 two-compartment sink, none of which are on K2.0 'EQUIPMENT SCHEDULE 1ST LEVEL' or K1.0: please issue a second-level K schedule or confirm the mezzanine bar equipment is outside the KEC package. Sheets / documents: A-5.20, A-2.20 KN27, P-4 (BS-3, BS-4, BS-5), P-6 calc, K1.0 / K2.0. Bid impact: Bid-letter items F&B equipment and Plumbing: the mezzanine bar equipment has no lines at all; P-014..P-016 (BS-3, BS-4, BS-5) are priced on P-4 models only and their water / waste connections and the glass washer are unpriced.
Suggestion:
Issue K1.1 / K2.1 for the mezzanine.
Answer: |  |  |  | Date Answered:

## RFI #014
Request for Information #014
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
First-floor bar sink counts | Plumbing / Foodservice |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
P-2 draws BS-1 (dump sink) x1 and BS-2 (hand sink) x2 while K2.0 schedules dump sink item 63 x2 and underbar hand sink item 71 x1: please confirm the count and location of each bar sink. Sheets / documents: P-2, K2.0 items 63 and 71. Bid impact: Bid-letter items Plumbing and F&B equipment: rough-ins P-012 / P-013, fixtures FE-63 / FE-71, vents (P-031) and I.W. connections (P-064) carry conflicting quantities.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #015
Request for Information #015
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Three new lighting / sound panels and re-feed of the Dillons loads | Electrical |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
Addendum 3 locates three new panels for lighting and sound on the mezzanine east wall by the stair but gives no rating, voltage, feeder size, feeder length or source, and the Dillons panel to be removed carries 25 circuits (lighting, 7 TV-outlet lines, 3 POS lines, emergency lights, refrigerator, 220 V deep fryer) with no new home: please issue the new panel schedules, feeders and source, and state which Dillons loads are re-fed and from where. Sheets / documents: Addendum 3, E-2.0, E-2.1 (Dillons schedule). Bid impact: Bid-letter item Other required scope (electrical power): lines E-011 (3 panels), E-012 (feeders) and E-007 (Dillons removal / re-feed) cannot be priced.
Suggestion:
Add the three panels to the E-2.0 single line with feeder sizes.
Answer: |  |  |  | Date Answered:

## RFI #016
Request for Information #016
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Distribution panel DP / switchboard data and legacy schedules | Electrical |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The E-2.1 schedule shows panel DP as 200 A bus MLO while E-2.0 shows '(E) main switchboard DP 400 A' with a '(E) 700A 3P' main and '800A' bus, E-2.0 feeder 2 goes to '(E) panel DMA' (no schedule), feeder 7 'DW hood exhaust 50A/3P' differs from DP ckt 12 'DM Hood Exhaust 20A/1P', panel KA lists the legacy tenant's loads (ice tea brewer, soup wells, mixer 60A/3P) that do not match K2.0, panel A prints '-' for every breaker size and HA circuit 'Switch - ?': please issue corrected single-line and panel schedules for the new loads. Sheets / documents: E-2.0, E-2.1 (DP, KA, HA, A schedules). Bid impact: Bid-letter item Other required scope (electrical power): panel rewiring lines E-001..E-006 and E-013 are counted by legacy circuits only; the feeder and breaker sizes for the hood exhaust and kitchen equipment cannot be fixed.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #017
Request for Information #017
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Lighting circuiting and the Lutron Athena control devices | Electrical / Lighting |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
No lighting plan or circuiting exists on the E-sheets for the A-3.70 fixtures (total connected A1 77 W, B1 462 W, C1 291 W, F1 418 W, G1-G21, exit / EM 125 W) and the Lutron Athena dimming banks (DB) and dimming switches appear only in the RCP legends with one switch placed: please issue the lighting circuits, panel assignments and the count and location of dimming banks and dimming switches. Sheets / documents: A-3.70 (IFB 9/9/2026 and plan check 8/18/2026), A-3.12, A-3.22, E-2.1. Bid impact: Bid-letter item Lighting: lines E-128 (lighting control), E-132 (lighting branch circuits and panel capacity) and E-129 (switching beyond 3 placed switches) are not quantifiable.
Suggestion:
Issue E-4.x lighting plans with the Athena device schedule.
Answer: |  |  |  | Date Answered:

## RFI #018
Request for Information #018
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Light fixture counts and governing issue of A-3.70 | Lighting |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The IFB A-3.70 quantities differ from the RCP tags (B1 33 vs 28, F1 22 vs 24, G20 16 vs 15, X1 17 vs 18, Y1 17 vs 15, Y2 14 vs 11, Y3 8 vs 9, G21 qty 16 vs one 98-ft run) and the plan-check A-3.70 (8/18) differs again (A1 qty 1, G1-G5 as DiodeLED Valent, Y1 15, Y3 9, D1 TRIAC/ELV dimming; the C2 spec sheet is image-only): please confirm which issue of A-3.70 governs and the quantity of each type. Sheets / documents: A-3.70 (IFB qty vs RCP tags A-3.12 / A-3.22; plan-check issue). Bid impact: Bid-letter item Lighting: fixture lines E-101..E-127 are priced on the IFB quantities; the differences change the fixture package by up to 5 units per type and the G21 handrail LED by 16 vs 98 LF.
Suggestion:
Re-issue A-3.70 with quantities reconciled to the RCPs and a legible C2 cut sheet.
Answer: |  |  |  | Date Answered:

## RFI #019
Request for Information #019
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Trim-kit schedule, 24 V drivers / transformers and open strip-light lengths | Lighting |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-3.70 refers to a 'Trim Kit Schedule' for the A1 ordering matrix that is not drawn on either issue, note A refers to sheet 'EQ-2.10' and note D to 'Electrical Dwgs for Transformer specifications' that are not in the set, the 24 V DC drivers for the Omni Light / CORE strip lights and the remote drivers for C1 pendants and A1 downlights are not scheduled, G16-G18 catalog lengths print "X'" and G21 wattage prints '150w, 134234lm': please issue the trim-kit schedule, the driver / transformer schedule and the missing lengths. Sheets / documents: A-3.70 (notes A and D, A1 remarks, G16-G18, G21). Bid impact: Bid-letter item Lighting: lines E-122 (drivers / power supplies), E-131 (trim kits) and E-117 (G16-G18, 3 EA with no length) cannot be quantified; the strip-light package (E-107..E-121, 707 LF Omni + 119 LF CORE) cannot be quoted complete.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #020
Request for Information #020
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Existing water heater model and replacement | Plumbing |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
K2.0 item 14, P-5 and P-6 name the existing roof water heater as A.O. Smith BTH-250 (100 gal, 250 MBH), the P-4 fixture schedule says BTH120 (60 gal, 120 MBH), the ACCO assessment reports a Bradford White BWCV0400 per the 2009 plans (not verified) and recommends replacement, and the P-5 calculation requires 320 GPH / 180 MBH minimum: please confirm the existing unit and whether its replacement, with the P-5 trim (expansion tank, vacuum relief, seismic straps, enclosure), is in the bid. Sheets / documents: K2.0 item 14, P-4 fixture schedule, P-5, P-6, ACCO site assessment (June 2026). Bid impact: Bid-letter item Plumbing: line P-001 is carried as existing; a replacement heater, its gas (P-061, 250 CFH), venting and electrical (E-019) are not in any bid line.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #021
Request for Information #021
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Water service size and point of entry | Plumbing |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The P-1 sizing form states 'meter size 3"' (and 'loss thru 2.0" meter') while P-2 shows the '(E) 2" water meter in sidewalk vault' and ACCO estimates 2.5 in copper with the point of entry not verified (open wall / floor to verify): please confirm the meter size, whether a new meter or service is required, and the point of entry. Sheets / documents: P-1 (sizing form), P-2, ACCO site assessment item 4. Bid impact: Bid-letter item Plumbing: line P-037 (2-1/2 in service, 60 LF) and P-021 (2-1/2 in PRV) are priced on P-2; a meter upgrade or new service is not in the bid.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #022
Request for Information #022
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Gas piping sizes, hood gas valve and gas meter / seismic valve | Plumbing |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
P-7 labels the whole 24 ft cook-line manifold 2 in with a '2" MECH./ELECT. ANSUL VALVE' while M-7 specifies a 2.5 in 'SC ELECTRICAL' valve supplied by CaptiveAire, the P-7 riser diagram sizes the manifold 1.5 / 1.25 / 1 in with 1 in drops while K2.0 lists 3/4 in appliance connections, and ACCO reports an existing 3,000 CFH rotary meter with an approved seismic valve on the 3 in main while P-7 shows a new seismic valve: please confirm the manifold and drop sizes, the gas-valve size, and whether a new SoCalGas meter and seismic valve are required. Sheets / documents: P-7 (riser diagram and plan), M-7 (gas valve table), K2.0 gas column, ACCO item on the gas meter. Bid impact: Bid-letter items Plumbing and F&B equipment: lines P-059..P-063 (gas piping by size, drops, seismic valve) and M-017 / FE-55 (gas valve) carry conflicting sizes.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #023
Request for Information #023
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Backflow prevention | Plumbing |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
P-4 schedules BFP-1 as a Wilkins 975XL 3/4 in reduced-pressure device while the P-1 form states 'backflow prevention device not required per rule 16-D' and the P-1 plan-check note requires RP devices on carbonators: please confirm which backflow devices are required, their sizes and locations. Sheets / documents: P-4 (BFP-1), P-1 (sizing form and plan-check note). Bid impact: Bid-letter item Plumbing: line P-020 (BFP-1) and the water-heater trim backflow (P-002) cannot be fixed; carbonator RP devices (soda systems items 81 / 103) are not in any line.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #024
Request for Information #024
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Fixture and faucet specifications P-4 vs K2.0 vs A-5.12 | Plumbing / Foodservice |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The fixture models differ between sheets - KS-1 John Boos 2PB1824-2D24 (P-4) vs GSW SE18183D20 (K2.0 #88), DM-1 CMA EST (P-4) vs CMA-180C (K2.0 #98), MS-1 faucet T&S B-0133-ADF-12B (P-4) vs B-0665-BSTR (K2.0 #20), L-1 basin Kohler K-2035-8 (A-5.12) with Sloan EBF-415 faucet (P-4), WC-1 Kohler K-3609-T tank type (P-4) vs the P-1 form's flush-valve Caroma list (x6) and UR-1 x2 - and no faucets are scheduled for hand sinks 31 / 93: please state which schedule governs each fixture and the hand-sink faucets. Sheets / documents: P-4 fixture schedule, K2.0 items 20, 31, 88, 93, 98, A-5.12, P-1 fixture list. Bid impact: Bid-letter items Plumbing and F&B equipment: lines P-004..P-011, FE-20, FE-31, FE-88, FE-93, FE-98 are quoted on one of two models each; the WC-1 tank vs flush-valve choice changes the rough-in and water supply.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #025
Request for Information #025
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
K2.0 model numbers vs the cut-sheet book | Foodservice |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The K2.0 model strings differ from the cut-sheet book for items 1 (MQ21XXQ vs MQ2148G), 36 (14XXFG vs 1436FG), 45 (R295-CL vs R295-CLX), 52 (ATFS-40 vs ATFS-40ES-NG), 63 (TSF18DS vs TSF18DS-TR), 67 (TSD21 vs TSF21DB), 73 / 105 (KM-520MAJ vs export KM-520MAJ-E), 75 (EV9329-52 vs EV9329-72) and 104 (the page stamped 'Item #104' is an Atosa MGF8401GR), and items 1 / 10 / 13 / 36 carry 'XX' length placeholders with no post or unit counts: please state which governs and the shelving sizes and unit counts. Sheets / documents: K2.0 items 1, 36, 45, 52, 63, 67, 73, 75, 104, 105; cut sheet book. Bid impact: Bid-letter item F&B equipment: the dealer quote for these 11 lines cannot be requested on a single model; the Metro shelving lots (FE-1, FE-10, FE-13, FE-36) have no quantity to quote.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #026
Request for Information #026
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Walk-in manufacturer and remote refrigeration package | Foodservice / Refrigeration |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
K2.0 names 'AIRCOOLER' for items 7-12 while the walk-in drawings K8.0-K8.3 are by Arctic (Q228534) with Russell R-454A outdoor condensing units: please confirm the specified manufacturer and whether the condensing units, line sets, A2L leak detection, controls, the 6 in roof platform and the refrigeration subcontract are in the KEC package or the GC's bid. Sheets / documents: K2.0 items 7-12, K8.0-K8.3 (Arctic Q228534, Russell units), KN refrigeration notes 7-8, 12. Bid impact: Bid-letter item F&B equipment: lines FE-7, FE-8, FE-9.1, FE-9.2, FE-11, FE-12 (walk-in box, coils, condensing units) have no published price and no furnishing party; the roof platform (M-052, GC per KN note 12) and refrigeration connections (E-015) cannot be assigned.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #027
Request for Information #027
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Hood fire-suppression system scope split and permit | Foodservice / Electrical / Plumbing |  |  | Scope
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
K7.0 shows a 4.0/4.0/4.0 gal TANK system in a 60 in wall-mount utility cabinet 'to be hung by others' and M-7 makes the fire-suppression permit a deferred submittal by the fire installer: please confirm the scope split for the gas valve installation (plumber), the remote pull station (KD detail), the shunt-trip breaker and contactors (EC per KN note 31), the cabinet hanging, and who holds the deferred permit. Sheets / documents: K7.0/K7.1, KD details, M-7, K2.0 item 55. Bid impact: Bid-letter items F&B equipment, Mechanical, Plumbing and Other required scope: lines FE-55 / M-016 / M-017 / E-016 and the permit (G-03 'pulled by others') cannot be allocated between the vendor, the fire installer, the plumber and the electrician.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #028
Request for Information #028
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Fire-alarm devices and hood fire-system interface | Low voltage / Fire alarm |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
M-7 assigns the hood fire-system interface (manual activation device, remote firestat, fire-alarm contact to the building FA panel, trouble contact, CASlink RJ-45) to an alarm contractor and no fire-alarm device plan exists for the tenant space: please issue the fire-alarm scope for the tenant improvement and state who contracts the alarm work and its permit. Sheets / documents: M-7 (alarm contractor requirements), E-2.2 (EPB FA terminal cabinet). Bid impact: Bid-letter item Low Voltage: line LV-005 (fire-alarm interface) is a lump sum with no device count; the fire-alarm permit is 'pulled by others' (G-03).
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #029
Request for Information #029
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Dimensions of the custom stainless-steel items | Foodservice |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
Thirteen CUSTOM ST/ST lines on K2.0 (16, 17, 33, 34, 38, 39, 41, 58 wall flashing, 61 service bar top, 84, 94 clean dishtable, 100 soiled dishtable, 101 sorting shelf) have no cut sheets and no dimensions on K1.0: please issue lengths, depths, heights and construction (gauge, backsplash, sink bowls, undershelves) for the fabrication quotes. Sheets / documents: K2.0 items 16, 17, 33, 34, 38, 39, 41, 58, 61, 84, 94, 100, 101; K1.0; KD. Bid impact: Bid-letter item F&B equipment: 12 fabricator lines (FE-16, 33, 34, 38, 39, 41, 58, 61, 84, 94, 100, 101) cannot be quoted; the wall flashing length also depends on RFI 009.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #030
Request for Information #030
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
K2.0 electrical data gaps | Foodservice / Electrical |  |  | Unreadable / incomplete
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
K2.0 prints '*' for the amps of items 6 (208 V floor mixer), 9 and 12 (208 V refrigeration, K8.2 gives MCA 15), 57 (208 V 3 ph exhaust fan system), 76 (120 V ice machine, no CW entry although item 75 feeds it) and 97 (120 V Type II hood); item 27 Ovention S1200 'DOUBLE STACK' prints one 26.0 A value with 'each deck requires separate circuit' (one or two ovens?); item 98 CMA-180C is scheduled 208/3 20 A while the cut sheet gives 24 A without booster or 78 A at 208/1 with the 180 F booster that K0.0 note U requires: please provide the missing loads and confirm the oven count and the booster. Sheets / documents: K2.0 items 6, 9, 12, 27, 57, 76, 97, 98; K0.0 note U; K8.2. Bid impact: Bid-letter items F&B equipment and Other required scope (electrical power): connections E-014 / E-015 and the dealer lines FE-27 (one vs two ovens) and FE-98 (booster model) cannot be fixed.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #031
Request for Information #031
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Vent routing, sizes and tie-in to the existing vent stack | Plumbing |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
Vent piping is not routed on P-3 / P-4 (only '2" V.U.F.' x3 and the island-vent detail are shown), the P-4 VENT LINE DATA pipe-size column is cut off at the sheet edge, and the tie-in to the (E) 4 in vent stack is not shown: please issue the vent routing, sizes and point of connection. Sheets / documents: P-3, P-4 (vent line data, pipe-size column cut off), P-6 island-vent detail, ACCO. Bid impact: Bid-letter item Plumbing: line P-031 (vent piping for all new fixtures) has no LF and no sizes.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #032
Request for Information #032
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Trenching for the new sanitary piping | Plumbing / Concrete |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-9.10 detail 6 (utility trench patch) gives no trench width, the (E) slab thickness is 'match (E)', the branch trench lengths must be scaled from P-3, the split between trenched and basement-hung pipe is not derivable (ACCO) and the openings of the 9 floor drain / floor sink / trench-drain infills are not stated: please state the trench width and depth, the slab thickness, which runs are hung below the basement ceiling, and the infill sizes. Sheets / documents: A-9.10 detail 6, P-3, A-1.10 KN6 / KN16, ACCO basement findings. Bid impact: Bid-letter items Plumbing and Demolition: lines P-036 (189 LF saw-cut, trench and backfill), D-14, D-15, D-16, P-035 and the Cal/OSHA excavation permit (G-05, trenches 5 ft or deeper) are not quantifiable.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #033
Request for Information #033
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
First-floor existing restrooms: flush-valve and faucet retrofit | Plumbing |  |  | Scope
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The ACCO assessment (item 3) reports the first-floor restroom flushometer valves and faucets as non-compliant with CEC / Title 24 and the P-1 form lists Caroma flush valves (x6), waterless urinals (x2) and faucets, but P-2 / P-3 show the (E) restrooms as 'no changes' with re-piped headers only: please confirm whether the retrofit of the 10 existing fixtures is in the bid. Sheets / documents: ACCO site assessment item 3, P-1 fixture list, P-2 / P-3. Bid impact: Bid-letter item Plumbing: line P-070 (10 EA retrofit) and the re-piped (E) restroom headers P-051 (sizes not printed) cannot be priced.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #034
Request for Information #034
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Backwater valve at 1704 N Vine | Plumbing |  |  | Scope
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
ACCO reports the 6 in PVC backwater valve about 10 ft deep in the 1704 N Vine space, which picks up all gravity waste, with its flapper lodged open, and P-3 does not address it: please state whether the repair or replacement of the backwater valve is in the bid. Sheets / documents: ACCO site assessment (backwater valve), P-3. Bid impact: Bid-letter item Plumbing: line P-068 has no scope; an excavation 10 ft deep inside the occupied restaurant would also affect phasing (G-21).
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #035
Request for Information #035
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Items 102-106 'FOR 2ND LEVEL' | Foodservice |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
K2.0 marks items 103 (soda system) and 104 / 105 / 106 'FOR 2ND LEVEL' yet K1.0 places items 102-106 on the first floor south of the scullery by the dumbwaiter; item 102 'REFRIGERATOR/HTD. CAB' model RDH132WUT-HHS has no manufacturer and no cut sheet, and item 103 carries no soda-vendor remark unlike items 80 / 81: please confirm the location of items 102-106, what item 102 is, and whether item 103 is soda-vendor furnished. Sheets / documents: K1.0 / K2.0 items 102-106, A-5.20. Bid impact: Bid-letter items F&B equipment and Plumbing: lines FE-102, FE-103, FE-104, FE-105, FE-106 and their water / I.W. connections (P-066, P-064) cannot be quoted or located.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #036
Request for Information #036
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
'TYP.' column enclosure removals and column exposures | Demolition |  |  | Unreadable / incomplete
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
Keynotes KN9 (A-1.10) and KN7 (A-1.20) 'remove decorative non-bearing walls around structural columns' and KN18 (A-1.10) / KN11 (A-1.20) 'expose (E) concrete columns, patch and repair' carry 'TYP.' with 5 and 2 tag instances while 17 / 18 column symbols exist in the tenant area: please state which columns are enclosed and to be exposed, and the enclosure construction and height. Sheets / documents: A-1.10 KN9 / KN18, A-1.20 KN7 / KN11. Bid impact: Bid-letter items Demolition and Interior finishes: lines D-07 (5 EA by tag) and D-25 (2 EA) and the column patch / repair cannot be quantified.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #037
Request for Information #037
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Dumbwaiter opening and beams | Structural |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The dumbwaiter floor opening is 4'-8" x 4'-0" on A-1.20 and 4'-2" x 4'-0" on the A-6.30 demolition plan, A-6.30 calls a '(N) 10"x22" steel beam, see S-2.20' while S-2.20 shows three W10x22 and 5/S-3.10 'W10x per plan', and the (E) waffle-slab thickness at the cut is not stated: please confirm the opening size, the beam sections and the slab thickness. Sheets / documents: A-1.20, A-6.30, S-2.20, 5/S-3.10. Bid impact: Bid-letter items Other required scope and Demolition: lines S-13 (W10x22 x3 with 2-hr SFRM), D-17 (slab cut 16.7 SF) and the dumbwaiter shaft framing depend on the answer.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #038
Request for Information #038
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
ADA lift pit and '(N) structural beam below' | Structural |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-6.21 KN12 refers to a '(N) structural beam below' the ADA lift 'see S-2.10' that is not on S-2.10, and the lift pit slab thickness, reinforcing and concrete strength are not detailed: please issue the pit and beam details. Sheets / documents: A-6.20, A-6.21 KN12, S-2.10, 6/S-3.20. Bid impact: Bid-letter item Other required scope: lines S-09 (pit base and beam), D-28 (pit cut 21.1 SF) and the special inspection trigger (G-15, concrete above 2,500 psi) cannot be priced.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #039
Request for Information #039
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Stair 1 landing supports | Structural |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
S-2.10 places the two 'HSS4x4x1/4' labels on diagonal lines at the landing corners while 5/S-3.20 draws vertical posts, and the landing is dimensioned 4'-4" x 3'-9": please confirm whether the landing is supported on vertical posts or kicker braces and the landing size. Sheets / documents: S-2.10, 5/S-3.20, A-6.10 / A-6.12. Bid impact: Bid-letter item Other required scope: lines S-03 (HSS8x4 landing beams), S-04 (landing framing), S-05 (posts 15.9 LF) and S-06 (base plates, 8 epoxy rods) depend on the support type.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #040
Request for Information #040
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Exit-stair landing size, pan fill and guard | Structural |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The exit-stair landing is dimensioned 5'-0" x 4'-0" on A-6.10 while the ENERCALC landing beam spans 6.0 ft and a 6'-3" dimension sits outside the landing, the pan-fill concrete depth and strength are not stated (special inspection applies above 2,500 psi), and the A-6.11 sections show a picket guard where the plan shows walls on both sides: please confirm the landing size, the fill depth and strength, and whether a guard is required. Sheets / documents: Exit-stair set: A-6.10, A-6.11, S-2.10, S-3.10, ENERCALC. Bid impact: Bid-letter item Stairs & railing: lines X-03 (pan fill, no depth), X-04 / X-05 (landing beams and framing), X-12 (guard, no LF) and the inspection line G-15 cannot be fixed.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #041
Request for Information #041
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Typical stud size and the 2-hr wall type 1A | Structural / Framing |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The S-2.10 / S-2.20 legend states '400S162-54 @ 16" typ. all walls', the S-1.10 schedule states '362S162-54 @ 16"' for the ground and second levels, A-2.10 wall note 1 prints 400S162-54 and A-2.20 wall note 1 prints '3-5/8" 20 GA' studs for the same wall tag: please confirm the stud size and gauge for wall types 1 and 2 and whether the 2-hr wall type 1A extends to the rated deck. Sheets / documents: S-2.10 / S-2.20 legend, S-1.10 schedule, A-2.10 wall note 1, A-2.20 wall note 1. Bid impact: Bid-letter item Interior walls: all new partitions (A-001..A-033 by tag, S-18, 527.7 LF of 16 GA studs on A-041) and the dumbwaiter shaft walls are priced on one of the sizes; the type 1A height fixes its 2-layer GWB area (A-035).
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #042
Request for Information #042
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Sloped mezzanine floor for exit-stair headroom | Structural |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-1.20 KN17 shows a 26 SF sloped mezzanine floor for the exit-stair headroom clearance with no structural detail on S-2.20 or the exit-stair S-sheets: please issue the construction of the sloped floor and state under which permit it is built. Sheets / documents: A-1.20 KN17, S-2.20, exit-stair S-sheets. Bid impact: Bid-letter items Other required scope and Stairs & railing: line S-15 has no construction to price and the permit split (TI vs 26016-10000-18605) is open.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #043
Request for Information #043
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Existing door access to the main building and untagged mezzanine wall | Architectural / Demolition |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The exit-stair A-0.20 notes an '(E) door access to the main building (not code compliant)' to be removed without location, size or infill construction, and A-1.20 draws an untagged dashed double-line wall (14.4 LF) inside the exit-stair limit of work: please locate and size the door removal and infill, and state under which permit the untagged wall is removed. Sheets / documents: Exit-stair A-0.20, A-2.10, A-1.20 (wall W1). Bid impact: Bid-letter items Stairs & railing and Demolition: lines X-20 (door removal and infill) and D-24 (wall 14.4 LF) cannot be quantified or assigned to a permit.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #044
Request for Information #044
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Vector S-2.10 / S-2.20: shear-wall marks, holdowns, saddles, headers | Structural |  |  | Unreadable / incomplete
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The S-2.10 / S-2.20 sheets on hand are 110 dpi rasters on which the Sure-Board shear-wall marks (S-1.10 schedule marks 1-4) and S/HDU4 / S/HDU6 holdown symbols are not legible, the box-beam column-saddle count (4/S-3.10) and the attic joist extents cannot be confirmed, and the headers at new wall openings are 'see detail' with no count: please issue vector S-2.10 / S-2.20 (or legible prints) with the shear-wall and header schedule applied. Sheets / documents: S-2.10, S-2.20, S-1.10 (raster only at 110 dpi), 4/S-3.10, A-9.10 headers. Bid impact: Bid-letter item Other required scope: lines S-17 (Sure-Board shear walls and holdowns), S-16 (headers), S-12 (attic joist extents, 1,538 SF) and the saddle anchors for G-14 special inspection cannot be quantified.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #045
Request for Information #045
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Hazardous-materials survey | General |  |  | Scope
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
No bid document requires or provides a hazardous-materials survey for the 1920s building (ceiling coffers, plaster, flooring mastics, pipe insulation to be demolished): please state whether a survey exists, its findings, and whether any abatement is in the bid. Sheets / documents: General notes, A-0.00. Bid impact: Bid-letter items Demolition and Other required scope: line G-28 (survey / abatement) has no scope and the coffer / plaster demolition (D-20) could become abatement work.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #046
Request for Information #046
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Untagged dashed enclosure in the existing kitchen | Demolition |  |  | Unreadable / incomplete
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-1.10 draws an untagged dashed double-line enclosure 12.3 x 14.7 ft in the (E) kitchen next to the two KN4 walk-ins: please confirm whether it is a third walk-in box, an equipment enclosure or a partition to be removed. Sheets / documents: A-1.10 (untagged enclosure 12.3 x 14.7 ft). Bid impact: Bid-letter item Demolition: line D-02 (181 SF) is priced as a walk-in removal by assumption.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #047
Request for Information #047
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Exit-stair steel finish and exit signage | Structural / Painting / Electrical |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The finish of the exit-stair steel (paint system or galvanizing) is not specified (stair 1 calls P-6) and the exit-sign symbols on the A-0.20 exit-analysis plans are legible for one location only: please specify the steel finish and the exit sign / egress signage count and circuit for the new exit stair. Sheets / documents: Exit-stair S-0.10, A-6.10 / A-6.11, A-0.20. Bid impact: Bid-letter item Stairs & railing: lines X-23 (finish) and X-22 (exit signs) have no specification or count.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #048
Request for Information #048
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Exit-stair storefront and door hardware | Architectural / Glazing |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The fixed storefront panel between the two new exit doors (4'-8" wide, height taken from the (E) door) has no mullion layout or frame section, and the panic hardware and closer sets for the two storefront doors and the 1-hr exit-access door are not specified: please issue the storefront elevation / section and the hardware sets. Sheets / documents: Exit-stair A-2.10 KN4 / KN5, A-6.10. Bid impact: Bid-letter item Stairs & railing: lines X-15, X-16 (framing LF) and X-17 (hardware) are priced on assumed products.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #049
Request for Information #049
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Item 46 Rational combi oven (existing, relocated) | Foodservice |  |  | Unreadable / incomplete
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
K2.0 item 46 'RATIONAL #I COMBI CLASSIC' (cell highlighted, size not given, plumbing columns blank) is existing relocated while K3.0 shows two +68 in rough-ins: please state the model / size and its water, drain and electrical requirements. Sheets / documents: K2.0 item 46 (highlighted cell), K3.0. Bid impact: Bid-letter items Owner-provided equipment install and Plumbing: the combi rough-in and filter (FE-45, P-058) and the 208 V 3 ph connection (E-015) cannot be fixed.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #050
Request for Information #050
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Item 22 grease interceptor connection size | Plumbing / Foodservice |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
K2.0 gives item 22 Big Dipper W-350-IS a 4 in waste while the cut sheet shows 3 in inlet / outlet and K3.0 notes 'VFY. W/ PLUMBER': please confirm the connection sizes and the 3 in drain / 2 in vent of P-3 GT-1. Sheets / documents: K2.0 item 22, K3.0 note, cut sheet. Bid impact: Bid-letter item Plumbing: line P-019 / P-025 (3 in run to GT-1) and the direct waste of KS-1 (P-065) are sized on P-3.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #051
Request for Information #051
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Plan vs schedule quantity differences | Foodservice |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
K1.0 draws item 95 (slant rack shelf) twice (scullery and service bar) against a scheduled quantity of 1, item 2 lockers as one bank against qty 5, items 1 and 10 as 6 and 5 shelving units against '1 LOT', and single bubbles for items 26 / 36 / 89 scheduled 2 each: please confirm the quantities. Sheets / documents: K1.0 vs K2.0 (items 1, 2, 10, 26, 36, 89, 95). Bid impact: Bid-letter items F&B equipment and Owner-provided equipment install: lines FE-95, FE-2, FE-1, FE-10, FE-26, FE-36, FE-89 carry the schedule quantity.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #052
Request for Information #052
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Existing storage area in the TI scope | Foodservice / Architectural |  |  | Scope
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
K2.0 items 1 (storage shelving) and 2 (five existing lockers, relocated) sit in the 'EXISTING STORAGE AREA' on K1.0: please confirm whether that area is inside the tenant-improvement scope and whether its finishes are touched. Sheets / documents: K1.0 (EXISTING STORAGE AREA), K2.0 items 1 and 2, A-2.10. Bid impact: Bid-letter items F&B equipment and Owner-provided equipment install: lines FE-1 and FE-2 and any finish work in that room.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #053
Request for Information #053
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Construction of existing elements to be demolished | Demolition |  |  | Unreadable / incomplete
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The drawings do not state the construction, height or material of the (E) ramp (KN10), raised platform and steps (KN12), curved stair to the mezzanine (KN11), mezzanine ceiling coffers and mouldings (A-1.20 KN14, 890 SF), the 72 mezzanine ceiling light fixtures (KN15), the mezzanine walls KN13 / KN4 (heights) or the extent of terrazzo patching (A-1.10 KN14): please provide them or confirm they are to be verified at a pre-bid site walk. Sheets / documents: A-1.10 KN10 / KN11 / KN12 / KN14, A-1.20 KN13 / KN14 / KN15, KN4. Bid impact: Bid-letter item Demolition: lines D-07..D-11, D-20..D-23 and D-26 are quantified by area or length only and cannot be priced by removal type.
Suggestion:
A scheduled pre-bid site walk would close this item.
Answer: |  |  |  | Date Answered:

## RFI #054
Request for Information #054
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Floor-to-floor heights for risers and hangers | Plumbing / Mechanical |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The vertical risers (basement to first floor, first floor to mezzanine, mezzanine to the second-floor roof) and the hood hanger-rod lengths are not dimensioned on any M- or P-sheet: please state the floor-to-floor and floor-to-roof heights at the riser locations. Sheets / documents: P-2, P-3, P-4, M-4 (vertical risers), M-6 (hanger rods). Bid impact: Bid-letter items Plumbing and Mechanical: lines P-030, P-050 (sanitary and water risers), P-061 (gas riser) and M-018 (hanger rods) are counted EA with no length.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #055
Request for Information #055
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Unlabeled pipe sizes on P-2 / P-4 | Plumbing |  |  | Unreadable / incomplete
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The re-piped (E) first-floor restroom CW / HW branch headers and fixture drops below the 2 in CW / 1 in HW labels on P-2 (41 LF) and the HW run to the mezzanine lavatories beyond the 1 in label on P-4 (27.5 LF) carry no sizes: please label them. Sheets / documents: P-2 (first-floor restroom headers), P-4 (HW beyond the 1 in label). Bid impact: Bid-letter item Plumbing: lines P-051 and P-055 (and their insulation in P-057) cannot be priced by size.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #056
Request for Information #056
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Mold Tough GWB 'wet areas' and head-of-wall fire sealant | Architectural / Framing |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The wall notes call Mold Tough GWB to 4'-0" 'at wet areas' without defining the wet areas, and the rated walls (types 1, 1A, AC, UL U404) call only acoustical sealant at the ceiling line with no head-of-wall fire-stop system: please define the wet-area rooms and the head-of-wall fire sealant / fire-stop assembly for the rated walls. Sheets / documents: A-2.10 / A-2.20 wall notes, A-9.10 detail 4, A-7.21. Bid impact: Bid-letter item Interior walls: lines A-046 (Mold Tough substitution 778 SF assumed) and A-045 (566 LF acoustical sealant) cannot be fixed; a rated head-of-wall system is not in any line.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #057
Request for Information #057
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Perforated metal column enclosures 'TYP.' | Architectural / Metals |  |  | Unreadable / incomplete
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
Keynotes KN21 (A-2.10) and KN23 (A-2.20) call perforated metal column enclosures floor to exposed ceiling around the (E) plumbing lines 'TYP.' with one tag per plan: please state how many columns receive the enclosure and the perforation pattern, gauge and finish (see also RFI 036 on the enclosures to be removed). Sheets / documents: A-2.10 KN21, A-2.20 KN23. Bid impact: Bid-letter item Interior finishes: line A-049 (4 EA assumed) has no count, product or finish to quote.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #058
Request for Information #058
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Extents of furring, beam soffit, hallway-opening ceiling and the 24 in low wall | Architectural / Framing |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The extent of the KN15 furring and patching of the (E) wall (two locations), the A-4.30 beam-enclosure soffit length, the A-4.31 GWB ceiling above the hallway opening and the A-2.20 KN17 24 in low wall around the sloped stair ceiling are not dimensioned or drawn in plan: please dimension them. Sheets / documents: A-2.10 KN15, Addendum 1 A-4.30 / A-4.31, A-2.20 KN17. Bid impact: Bid-letter item Interior walls: lines A-048, A-050, A-051, A-052 carry no quantity.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #059
Request for Information #059
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Day-2 scope in the base bid | Architectural |  |  | Scope
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-2.20 carries 27.4 LF of untyped walls on a 'Day2' layer, A-7.21 marks rooms 34 (BOH) and 35 (comedy club hallway) as Day2 with WC-4 finishes, and A-7.10 lists doors 18 and 39 (door 39 with a blank hardware set) in those rooms: please confirm whether the Day-2 walls, doors and finishes are in the base bid, an alternate, or excluded. Sheets / documents: A-2.20 (layer Day2), A-7.10 doors 18 / 39, A-7.21 rooms 34 / 35. Bid impact: Bid-letter items Interior walls, Doors & Hardware and Interior finishes: lines A-033, A-070, A-088, A-147, A-148 and the hallway-35 share of the B-5 LED base cannot be placed in the bid or excluded with certainty; more than one trade is affected.
Suggestion:
State the Day-2 scope on A-0.00 as an alternate or delete the Day2 layer from the bid set.
Answer: |  |  |  | Date Answered:

## RFI #060
Request for Information #060
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Door hardware gaps on A-7.10 | Doors / Hardware |  |  | Unreadable / incomplete
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
On A-7.10 fourteen doors are marked self-closing but their hardware sets omit closer HW-4, the HW-5 pull and HW-6 pivot products print '-', the cylinder count on the E01 pair is not stated, exit door 16 carries a keyed lever (HW-9) instead of exit hardware, the 60-minute doors 19 / 34 / 35 / E38 are type G with ventilation louvers, the hinge finish prints '-' for every door, door 39 has no hardware set and the provided-by cells for HW-9 / HW-10 are blank: please complete the hardware schedule. Sheets / documents: A-7.10 door and hardware schedule, door-type elevations, detail 7. Bid impact: Bid-letter item Doors & Hardware: lines A-089..A-103 and A-107 (hardware sets, hinges, louvers, thresholds) cannot be fixed; louvers in rated doors and a keyed lever on an exit door are code questions.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #061
Request for Information #061
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Window A glass type and location | Doors / Glazing |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
Window type A (3'-10" x 8'-1" fixed storefront unit) prints glass 'GL-1', which A-7.20 defines as the gold mirror for the 2nd-level bar, and its hexagon tag is not legible on A-2.10: please confirm the glass type for window A and that it is the fixed glass in the A-4.01 KN4 bay beside exit door 06. Sheets / documents: A-7.10 window schedule (type A), A-7.20 GL-1, A-4.01 KN4, A-2.10. Bid impact: Bid-letter items Doors & Hardware and Exterior finishes: lines A-108 / A-203 (window A, Arcadia TC470 acoustic storefront) cannot be specified.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #062
Request for Information #062
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
CLG-1D framing, 8'-0" band edge and K-13 specification | Ceilings |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The CLG-1D ceiling type gives no joist spacing or gauge, the edge of the 8'-0" dining band (A-3.12 KN3 'edge of attic') has no profile (a vertical GWB fascia 89.6 LF x 8'-9" is assumed), and the K-13 spray-applied insulation (AC-1) has no thickness, colour or NRC and no statement whether the coffer module is net or gross area: please issue them. Sheets / documents: A-3.12, A-3.22, A-7.21 (CLG-1D, K-13 / AC-1), A-7.20. Bid impact: Bid-letter item Ceilings: lines A-112..A-117 (3,050 SF CLG-1D, joists, fascia) and A-121 (3,773 SF K-13 gross) cannot be quoted to a product.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #063
Request for Information #063
Project: 2604 | Importance: | High |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Existing restrooms 11 / 12 / 13: scheduled new finishes and accessories | Architectural / Finishes |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-5.11 marks the (E) restrooms 11, 12 and 13 'no revision, reference only' while A-7.21 schedules new FL-7 / FL-8 tile, B-1 base, WT-1 / WT-2 wall tile and a refinished CLG-1A ceiling there and A-5.11 carries new keynotes 13, 15, 16, 21-23 (accessories): please confirm whether the (E) restrooms receive the scheduled new finishes and accessories (see also RFI 033 for the plumbing retrofit). Sheets / documents: A-5.11 ('no revision, reference only'), A-7.21, A-2.75, A-5.11 keynotes 13 / 15 / 16 / 21-23. Bid impact: Bid-letter items Flooring, Interior finishes and Plumbing: lines A-118 (417 SF ceiling), A-129 (371 SF of the 602 SF tile), A-135 (B-1 base), A-152 (510 SF wall tile) and A-193 (8 accessories) cannot be included or excluded; several trades are affected.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #064
Request for Information #064
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Flooring products, grout, floor preparation and transitions | Flooring |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-7.21 schedules FL-3 and B-3 at the mezzanine restrooms while A-7.20 marks both 'NOT USED' and A-2.76 shows FL-7 / FL-8 with GRT-1, the grout joint is 1/16 in on A-5.11 and 1/8 in on A-5.12 / A-7.20, the FL-9 terrazzo manufacturer is 'TBD', the WT-1 / WT-2 pattern split is not drawn, and no floor-preparation / moisture-testing or transition-strip profile is specified: please resolve the products and specify preparation and transitions. Sheets / documents: A-7.20 (FL-3, B-3 'NOT USED', FL-9, GRT-1), A-2.75 / A-2.76 KN1, A-5.11 note 1, A-5.12 note 1. Bid impact: Bid-letter item Flooring: lines A-129, A-130, A-132, A-136, A-137 and A-151 cannot be quoted to a product or quantity.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #065
Request for Information #065
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Finish conflicts between A-7.21 and the Addendum 1 elevations | Finishes |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
Hallway 04 is WC-3 on A-7.21 but WC-8 with poplar moulding on A-4.26, the mechanical attic 25 is WC-8 on all four walls, doors and frames are P-1 on A-7.10 but frames P-2 (1st floor) and P-5 / doors WC-4 (mezzanine) on the Addendum, and the ADA lift lobby walls are P-4 on A-7.21 but WC-4 on A-4.32: please state which governs. Sheets / documents: A-7.21 vs Addendum 1 A-4.26 / A-4.30-A-4.33, A-7.10 finish column. Bid impact: Bid-letter item Interior finishes: lines A-142 (1,104 SF), A-143 (1,788 SF), A-145 (moulding grid 3,939 LF), A-170 (door paint), A-157 / A-150 (lift lobby) carry the Addendum reading and may change.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #066
Request for Information #066
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Fabric panels, drapery, gold wallpaper / film / mirror and unlisted finish codes | Finishes |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-7.20 leaves the WC-5 Tectum panel size, thickness and height (8'-0" vs 9'-1"), the TX-4 fabric product and fin panel sizes, the TX-1 location, the WC-6 / WC-7 products, the GL-1 mirror location and the drapery hardware HW-20 / HW-21, fullness and finished sizes open, and the Addendum / stair sheets use codes LM-1, LM-2, ST-2 / SL-2, STN-2, HW-22 and P-6 that have no A-7.20 entry: please complete the finish schedule. Sheets / documents: A-7.20 (WC-5, WC-6, WC-7, TX-1, TX-4, GL-1 and the unlisted codes LM-1/LM-2, ST-2/SL-2, STN-2, HW-20/21/22, P-6), Addendum 1 A-4.20-A-4.23. Bid impact: Bid-letter item Interior finishes: lines A-159, A-162..A-168, A-169 and A-180 cannot be quoted.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #067
Request for Information #067
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Stage platforms: size, height, LED base, fascia, steps | Millwork |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The mezzanine stage is 6 in AFF on A-2.20 KN22 but 10 in on A-4.30 detail 5 and has no outline for its three KN22 tags, and for both stages the LED base perimeter, the fascia finish and the steps or ramp to the 18 in main stage are not drawn: please issue stage plans and sections. Sheets / documents: A-2.20 KN22, Addendum 1 A-4.30 detail 5, A-2.10 KN18, A-2.75. Bid impact: Bid-letter items Interior finishes and Lighting: lines A-171 (64.5 SF main stage), A-172 (mezzanine stage, no area), A-173 and the stage share of the B-5 LED base (A-134) cannot be quantified.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #068
Request for Information #068
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Pick-up counter and bar opening | Millwork |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The pick-up counter is 34 in AFF with a 36 in opening on A-5.20 / A-2.20 KN13 while the bar opening on A-4.33 is 6'-0" wide with a countertop at 42 in AFF, the countertop material is not stated and the KegWorks foot rail has no model: please state the governing height, width, countertop material and rail model. Sheets / documents: A-5.20, A-2.20 KN13, Addendum 1 A-4.33 details 2 and 8. Bid impact: Bid-letter item Interior finishes: lines A-175 (stainless pick-up counter), A-176 (bar opening 6 LF), A-177 (foot rail) cannot be fabricated or quoted.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #069
Request for Information #069
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Light-beam fins: count, profile and height datum | Millwork / Ceilings |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The A-4.22 elevation shows 9 light-beam fins while A-3.22 shows 8 'CURVE UP' zones, the fin side-face profile needed for the P-3 paint and TX-4 fabric areas is not dimensioned, and the 7'-9" / 8'-8" / 10'-4" fin heights on A-4.22 have no stated datum against the 15'-9" CLG-1D labels on A-3.22: please confirm the fin count, profile and datum. Sheets / documents: Addendum 1 A-4.22 / A-4.22A, A-3.22, A-7.21. Bid impact: Bid-letter items Interior finishes, Ceilings and Lighting: lines A-174 (9 fins), A-122 (fin ceilings 168 SF), A-156 (P-3), A-165 (TX-4) and the 18 G5 strip lights (E-111, 17 ft each) depend on the fins.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #070
Request for Information #070
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Owner-furnished vs GC-furnished specialties | Specialties |  |  | Unreadable / incomplete
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The A-7.20 action column reads 'GC' on every row and its legend shading for 'owner to provide, GC to install' cannot be told from the print: please state who furnishes the reception desk, the three mirrors, the hook rail, the make-up counter and the table lamp shown on A-4.20 / A-4.21. Sheets / documents: A-7.20 legend / action column, Addendum 1 A-4.20 / A-4.21. Bid impact: Bid-letter items Interior finishes and Owner-provided equipment install: lines A-181, A-184..A-188 may be owner-furnished.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #071
Request for Information #071
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Fire extinguisher cabinets, signage and restroom accessory products | Specialties |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
The 'FE' legend entry on A-2.10 / A-2.20 has no symbols placed on the plans, the green-room signage type is not stated, and the restroom accessories on A-5.12 (grab bars, dispensers, mirrors, hand dryers) have no manufacturer or model: please locate the FE cabinets and specify the signage and accessories. Sheets / documents: A-2.10 / A-2.20 legend 'FE', A-5.12 KN15, 8 & 9/A-5.10, A-7.20. Bid impact: Bid-letter item Interior finishes: lines A-190, A-191, A-192 have no count or product.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #072
Request for Information #072
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
ADA lift model and pit size; dumbwaiter capacity and installer | Conveying |  |  | Conflict
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-6.22 specifies Garaventa Genesis Shaftway GVL-SW-120 while A-6.21 KN2 calls GVL-SW-144, the pit is 55-3/8 x 54-7/8 in (KN2) vs the 55-3/8 x 56-1/4 in shaftway of the specification, the McKinley 'elevator door' scope is not defined, and the Matot size K dumbwaiter is specified only as the 100-750 lb medium-duty class: please confirm the lift model and pit, the door scope, the dumbwaiter capacity and who installs each unit (see also RFIs 037, 038). Sheets / documents: A-6.21 KN2, A-6.22 (lift specification), A-6.30 (dumbwaiter). Bid impact: Bid-letter item Other required scope: lines A-200 (lift), A-201 (dumbwaiter), A-202 (pit access door) and the pit / shaft lines S-08, S-09, D-28 cannot be fixed.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #073
Request for Information #073
Project: 2604 | Importance: | Low |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Stair 1: P-6 paint, warning strips and riser LED strip | Finishes / Lighting |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
A-6.12 calls paint P-6 on the stair-1 steel that is not listed on A-7.20, the visual warning strips on the carpeted treads have no product (painting is 'acceptable' per note 7), and the 'LED strip for riser illumination' on A-6.12 is not in the A-3.70 lighting schedule: please specify the three items. Sheets / documents: A-6.12 (P-6, LED riser strip), A-6.10 general note 7, A-7.20, A-3.70. Bid impact: Bid-letter items Stairs & railing and Lighting: lines A-159 (63.7 LF P-6), A-195 (warning strips) and A-196 (60 LF riser LED) have no product.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #074
Request for Information #074
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Hollywood Blvd exit-door bay: metal panel, plaster patch, terrazzo step, handrails, granite | Exterior |  |  | Missing document
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
On A-4.01 the extent of the aluminum metal panel at the door head (KN12), the plaster patching at the removed-window jambs and head, the thickness and edge of the FL-9 black terrazzo step and its coordination with the Hollywood Walk of Fame sidewalk, the material of the handrails 'to match (E)' (KN7) and the reuse location of the salvaged granite base (KN8) are not stated: please detail the bay. Sheets / documents: A-4.01 (KN5, KN7, KN8, KN9, KN12, KN13), A-7.20 FL-9. Bid impact: Bid-letter item Exterior finishes: lines A-204..A-210 and A-130 are quantified from the 7'-4" bay width only; the Walk of Fame work may need a separate agency approval.
Suggestion:
Answer: |  |  |  | Date Answered:

## RFI #075
Request for Information #075
Project: 2604 | Importance: | Med |  | Date Created: | 2026-10-28
Hollywood Comedy Club |  |  |  | Bidding Phase
6263 Hollywood Blvd.
Los Angeles, CA 90028
Answer Company: | Answered By: |  |  | Co-Respondent:
Kelly Architects | Name
2404 Wilshire Blvd, suite 1E
Los Angeles, CA 90057
Author Company: | Authored By:
Owl Tower Construction Group, Inc. | Estimating, Owl Tower Construction Group, Inc.
CSLB #1108551
Torrance, CA
Phone:
Subject: | Discipline: |  |  | Category:
Stair 2 (1704 N Vine) finishes on Addendum 1 A-4.34 | Architectural / Finishes |  |  | Scope
Cc: Company Name: | Contact Name: |  | Copies: | Notes:
Kelly Architects | George Kelly |  | 1
Question: |  |  |  | Date Required:
Addendum 1 A-4.34 shows finishes for stair 2 at 1704 N Vine (WC-4 wallpaper, B-4 base painted P-5, LED tread inserts, ADA railing P-5) that are not in the exit-stair permit set: please state whether these finishes are in the TI bid, the exit-stair permit, or excluded. Sheets / documents: Addendum 1 A-4.34, exit-stair set (permit 26016-10000-18605). Bid impact: Bid-letter items Stairs & railing and Interior finishes: the exit-stair package (X-01..X-23) carries no finishes beyond paint, and the G19 / G20 stair-2 strip lights (E-118, E-119) and B-5 LED base depend on the answer.
Suggestion:
Answer: |  |  |  | Date Answered: